## Sheet1
Fault occurs between A & B, monitoring current values exceed thresholds, and Open certain CBs
A | B | Monitoring factors | Threshold | Open CBs | Fault location
CB_FDR1 | RLC load 1 | Current of feeder 1 | >500 | CB_FDR1 | Feeders
CB_FDR2 | RLC load 2 | Current of feeder 2 | >500 | CB_FDR2
CB_FDR3 | RLC load 3 | Current of feeder 3 | >500 | CB_FDR3
CB_FDR4 | RLC load 4 | Current of feeder 4 | >500 | CB_FDR4
CB_FDR1 | CB_TRSF1 | Fault_on_22BUS1_Current > 500 |  | CB1_22KV | 22KV BUS
CB_FDR1 | CB1_22KV
CB_FDR4 | CB_TRSF2 | Fault_on_22BUS2_Current > 500 |  | CB3_22KV
CB_FDR4 | CB1_22KV
CB_TRSF1 | Transformer1 | Fault_on_TRSF1_Current > 1000, Current of CB_TRSF1 > 500 |  | CB_TRSF1, CB1_66KV, CB2_66KV | Transformer
Within transformer1
CB_TRSF2 | Transformer2 | Fault_on_TRSF2_Current > 1000, Current of CB_TRSF2 > 500, |  | CB_TRSF2, CB3_66KV, CB2_66KV
Within transformer2
CB1_66KV | CB2_66KV | Current of CB1_66KV > 1000, Current of CB2_66KV > 1000, Fault_on_66BUS1_Current > 500 |  | CB_TRSF1, CB1_66KV, CB2_66KV | 66KV BUS
CB1_66KV | Transformer1
CB2_66KV | Transformer1
CB3_66KV | CB2_66KV | Current of CB3_66KV > 1000, Current of CB2_66KV > 1000, Fault_on_66BUS2_Current > 500 |  | CB_TRSF2, CB3_66KV, CB2_66KV
CB3_66KV | Transformer2
CB2_66KV | Transformer2